kano konoha 2023-6-1

ADW300/WIFI debug process

Preparation beforehand：

- 1.Hardware parts:

  - . a compute;r

  - . a meter;

  - a module that makes usb port to RS485;

  - Screwdriver and some wires;‘

- 2.Software parts

  - ADW300/WIFI debugging software

  - If you are the first time you use USB to 485, you may still need to install the driver. We provide the following drivers for installation.

- 3.How to connect USB to 485 and the meter

- The + sign on moduel is connected to 21 port , and the – sign on moduel is connected to 22 port.

- for example:

- Then power up the meter(Please keep the device's upper ranking state during debugging.).

- 二.Set your WIFI parameters

- 1.Open the exe file in the debugging software folder.

- 2. Choose the right language

- 3.Select the correct port

- 4.Click “Boardcast Read Address”

- If the device communicates normally, you will see the setting interface on the right. Like this:

- When the device communication is normal, the protocol of the current firmware will be prompted. If this is not the protocol you want, please communicate with us in time. Like this:

- 5.Click the wifi set button on the right

- You will see some WIFI connection settings and protocol choices

- 6.Set the wifi username and password

- Enter the wifi username and password in the box. Please don't forget to click the “Set” button

- If you set successfully, you will see the following interface:

- 7.Set the connection method of wifi

- If the connection is DHCP, Please just check DHCP .Like this:

- If the connection method is static IP, there is no need to check DHCP. The parameters below are set according to your parameters. Like this:

- If you set successfully, you will see the following interface:

- Tips: You can read Mac-Adderss in this box:

- The above is to set all the content of the wifi. The following is differently setting according to the in -meter protocol.

Debugging Method(Modbus-Tcp)

- Click the “Modbus-Tcp”

- 2.Choose correct mode

- First you should read the current mode, please click the “read” and choose the correct mode you need, then click the “set”.

- 3.Set Connection Parameters

- If you need server mode, you don’t need to set the gateway ip and port. But if you need the Client mode, you need to set the IP or domain and the port.

- Please don’t forget to click “set”.

Debugging Method(MQTT(basic))

- Click “MQTT(basic)”

- Parameters Description:

- IP/Domain Nme: choose type to connect your server.

- IP:enter IP to connect your server.

- Domain Name:Enter domain to connect you server.

- Port: Your server’s port.

- Port Number: fixed to 1.

- Upload interval: uint is minute, The minimum is 1 minute.

- MQTT username: Your server’s username.

- MQTT password: Your server’s password.

- UP_topic: The topic of the data needed to be uploaded .

- MQTT_QOS: fixed to 1.

- Tips: Please don’t forget to click “set”.

Debugging Method(HWIOT)

- Click “EIOT(Oversea)”

- Parameters Description

- If your meter can not connected to the platform, you can check the parameters of these places. Please read parameters first.

- IP/Domain Nme: choose type to connect your server.

- IP:enter IP to connect your server.

- Domain Name:Enter domain to connect you server.

- Port: Your server’s port.

- Port Number: fixed to 1.

- Upload interval: uint is minute, The minimum is 1 minute.

- The recommended parameters are shown below:

- Country: This is your country.

- UTC: This is your country’s UTC.

- SerialNum: This is the fourteen -bit coding of the two -dimensional code or side of your meter.

- QOS:Fixed to 1.

- Datanum: Fixed to 43.

- The following is an example: